## General
MATS Quarterly Compliance Report - General Information
This is not an official report. This file contains information used to create the MATS Quarterly Compliance Report
QualityAssuranceAndCert
ORISCode | 880102
Version | 1.3
MATS Quarterly Compliance Report
FacilityName | AES Puerto Rico, LP
FRSNumber | 1100121141805
Title40Part | 63
Subpart | UUUUU
Year | 2025
Quarter | 2
Comment | This quarterly compliance report is being submitted in XML in accordance with Sections 1-13 of Appendix E of the MATS Rule following the draft Quality Assurance and Certification reporting instructions (Dated August 2023) provided by the Agency on its ECMPS Re-Engineering Effort webpage. AES has requested assistance from EPA to resolve questions related to interpretation regarding sorbent trap sampling sorbent trap monitoring requirements during a period when the facility was trying to maximize the sampling period due to safety considerations while the stack elevator was out-of-service. The discussion was put on hold during the government furlough. However,while EPA has been contacted again, the Agency has not responded regarding the issue. While questions may remain, AES is required to submit this report by the deadline in MATS rule. For the purposes of this report, AES has assumed the data in question will be considered valid, should be included in the 30-day averages, and should not be considered downtime.

## Unit Information
Unit Information
This is not an official report. This file contains information used to create the MATS Quarterly Compliance Report
Unit ID | Last Tune-up Date
1 | 2025-11-09
2 | 2025-02-18

## Averaging Group
Averaging Group Configuration
This is not an official report. This file contains information used to create the MATS Quarterly Compliance Report
Parameter | Averaging Group ID | Unit Stack or Pipe ID
HG | GP1 | 1
HG | GP1 | 2

## Fuel Usage Data
Fuel Usage Data
This is not an official report. This file contains information used to create the MATS Quarterly Compliance Report
Unit ID | Calendar Month | Fuel Type | Quantity of Fuel Combusted | Fuel Usage Units of Measure | New Fuel Type | Performance Test Date (If Required for New Fuel)
1 | 10 | Bituminous Coal | 8307 | TON
1 | 10 | Distillate Oil | 0 | GAL
1 | 11 | Bituminous Coal | 58345 | TON
1 | 11 | Distillate Oil | 0 | GAL
1 | 12 | Bituminous Coal | 77936 | TON
1 | 12 | Distillate Oil | 0 | GAL
2 | 10 | Bituminous Coal | 67393 | TON
2 | 10 | Distillate Oil | 39000 | GAL
2 | 11 | Bituminous Coal | 73350 | TON
2 | 11 | Distillate Oil | 16430 | GAL
2 | 12 | Bituminous Coal | 57626 | TON
2 | 12 | Distillate Oil | 31500 | GAL

## Unit 1 PM Test
Performance Test Summary Data |  | This is not an official report. This file contains information used to create the MATS Quarterly Compliance Report
Summary Data
Unit/Stack ID | 1 | Test Number | Begin Date/Time | End Date/Time | Avg. Emission Rate | Comment
Parameter | PM | 1PM-Q4-2025-1 | 2025-12-04 09:10 | 2025-12-04 15:28 | 0.0097
Method Code | 5MATS
Emissions Limit | 0.03 | Run Data
Method 19 Equation | 19-7 | Run Number | Begin Date/Time | End Date/Time | Pollutant Conc. | Emission Rate | Sampling Time (min) | Sample Volume (dscm)
Timing of Test | on schedule | 1 | 2025-12-04 09:10 | 2025-12-04 10:58 | 0.0098337 | 0.0083 | 96 | 2.57
Avg Group Indicator | not part of averaging plan (test performed on unit/stack not included in averaging plan) | 2 | 2025-12-04 11:30 | 2025-12-04 13:18 | 0.015598 | 0.0132 | 96 | 2.57
|  | 3 | 2025-12-04 13:40 | 2025-12-04 15:28 | 0.0088907 | 0.0075 | 96 | 2.56
Units of Measure: |  | QA Parameters
Emission Limit | LBMMBTU | Run | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3
Pollutant Conc. | GDSCM | Parameter | ISOKENETIC | FILTERTEMP | LEAK | ISOKENETIC | FILTERTEMP | LEAK | ISOKENETIC | FILTERTEMP | LEAK
|  | Value | 105.5 | 320 | 0 | 105.5 | 321 | 0 | 104.1 | 320 | 0
|  | Pass/Fail | PASSED | PASSED | PASSED | PASSED | PASSED | PASSED | PASSED | PASSED | PASSED
Conversion Factors
|  | Run | 1 | 1 | 2 | 2 | 3 | 3
|  | Factor | O2D | FD | O2D | FD | O2D | FD
|  | Source | RM | DEFAULT | RM | DEFAULT | RM | DEFAULT
|  | Value | 5.8 | 9820 | 5.8 | 9820 | 5.8 | 9820

## Unit 1 HCl Test
Performance Test Summary Data |  | This is not an official report. This file contains information used to create the MATS Quarterly Compliance Report
Summary Data
Unit/Stack ID | 1 | Test Number | Begin Date/Time | End Date/Time | Avg. Emission Rate | Comment
Parameter | HCL | 1HCL-Q4-2025-1 | 2025-12-04 09:10 | 2025-12-04 15:28 | 0.0003
Method Code | 26A
Emissions Limit | 0.002 | Run Data
Method 19 Equation | 19-7 | Run Number | Begin Date/Time | End Date/Time | Pollutant Conc. | Emission Rate | Sampling Time (min) | Sample Volume (dscm)
Timing of Test | on schedule | 1 | 2025-12-04 09:10 | 2025-12-04 10:58 | 0.382 | 0.0003 | 96 | 2.56
Avg Group Indicator | not part of averaging plan (test performed on unit/stack not included in averaging plan) | 2 | 2025-12-04 11:30 | 2025-12-04 13:18 | 0.181 | 0.0002 | 96 | 2.56
|  | 3 | 2025-12-04 13:40 | 2025-12-04 15:28 | 0.301 | 0.0003 | 96 | 2.56
Units of Measure: |  | QA Parameters
Emission Limit | LBMMBTU | Run | 1 | 1 | 2 | 2 | 3 | 3
Pollutant Conc. | MGDSCM | Parameter | ISOKENETIC | LEAK | ISOKENETIC | LEAK | ISOKENETIC | LEAK
|  | Value | 100.5 | 0 | 100.5 | 0 | 101.1 | 0
|  | Pass/Fail | PASSED | PASSED | PASSED | PASSED | PASSED | PASSED
Conversion Factors
|  | Run | 1 | 1 | 2 | 2 | 3 | 3
|  | Factor | O2D | FD | O2D | FD | O2D | FD
|  | Source | RM | DEFAULT | RM | DEFAULT | RM | DEFAULT
|  | Value | 5.7 | 9820 | 5.9 | 9820 | 5.9 | 9820

## Unit 2 PM Test
Performance Test Summary Data |  | This is not an official report. This file contains information used to create the MATS Quarterly Compliance Report
Summary Data
Unit/Stack ID | 2 | Test Number | Begin Date/Time | End Date/Time | Avg. Emission Rate | Comment
Parameter | PM | 2PM-Q4-2025-1 | 2025-12-03 09:30 | 2025-12-03 16:38 | 0.0234
Method Code | 5MATS
Emissions Limit | 0.03 | Run Data
Method 19 Equation | 19-7 | Run Number | Begin Date/Time | End Date/Time | Pollutant Conc. | Emission Rate | Sampling Time (min) | Sample Volume (dscm)
Timing of Test | on schedule | 1 | 2025-12-03 09:30 | 2025-12-03 11:28 | 0.0253 | 0.0245 | 96 | 2.83
Avg Group Indicator | not part of averaging plan (test performed on unit/stack not included in averaging plan) | 2 | 2025-12-03 12:05 | 2025-12-03 13:53 | 0.0257 | 0.0252 | 96 | 2.64
|  | 3 | 2025-12-03 14:50 | 2025-12-03 16:38 | 0.021 | 0.0206 | 96 | 2.63
Units of Measure: |  | QA Parameters
Emission Limit | LBMMBTU | Run | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3
Pollutant Conc. | GDSCM | Parameter | ISOKENETIC | FILTERTEMP | LEAK | ISOKENETIC | FILTERTEMP | LEAK | ISOKENETIC | FILTERTEMP | LEAK
|  | Value | 103.2 | 321 | 0 | 100.9 | 320 | 0 | 102.5 | 320 | 0
|  | Pass/Fail | PASSED | PASSED | PASSED | PASSED | PASSED | PASSED | PASSED | PASSED | PASSED
Conversion Factors
|  | Run | 1 | 1 | 2 | 2 | 3 | 3
|  | Factor | O2D | FD | O2D | FD | O2D | FD
|  | Source | RM | DEFAULT | RM | DEFAULT | RM | DEFAULT
|  | Value | 7.7 | 9820 | 7.8 | 9820 | 7.8 | 9820

## Unit 2 HCl Test
Performance Test Summary Data |  | This is not an official report. This file contains information used to create the MATS Quarterly Compliance Report
Summary Data
Unit/Stack ID | 2 | Test Number | Begin Date/Time | End Date/Time | Avg. Emission Rate | Comment |  |  | Report the total sample volume, in dscm
Parameter | HCL | 2HCL-Q4-2025-1 | 2025-12-03 09:30 | 2025-12-03 16:38 | 0.0001 |  |  |  | report “GDSCM”. For Methods 26, 26A, and 29, report “MGDSCM”. For Method 30B, report “UGDSCM”.
Method Code | 26A
Emissions Limit | 0.002 | Run Data
Method 19 Equation | 19-7 | Run Number | Begin Date/Time | End Date/Time | Pollutant Conc. | Emission Rate | Sampling Time (min) | Sample Volume (dscm)
Timing of Test | on schedule | 1 | 2025-12-03 09:30 | 2025-12-03 11:28 | 0.1198 | 0.0001 | 96 | 2.83
Avg Group Indicator | not part of averaging plan (test performed on unit/stack not included in averaging plan) | 2 | 2025-12-03 12:05 | 2025-12-03 13:53 | 0.1285 | 0.0001 | 96 | 2.64
|  | 3 | 2025-12-03 14:50 | 2025-12-03 16:38 | 0.18 | 0.0001 | 96 | 2.63
Units of Measure: |  | QA Parameters
Emission Limit | LBMMBTU | Run | 1 | 1 | 2 | 2 | 3 | 3
Pollutant Conc. | MGDSCM | Parameter | ISOKENETIC | LEAK | ISOKENETIC | LEAK | ISOKENETIC | LEAK
|  | Value | 103.2 | 0 | 105.4 | 0 | 101.7 | 0
|  | Pass/Fail | PASSED | PASSED | PASSED | PASSED | PASSED | PASSED
Conversion Factors
|  | Run | 1 | 1 | 2 | 2 | 3 | 3
|  | Factor | O2D | FD | O2D | FD | O2D | FD
|  | Source | RM | DEFAULT | RM | DEFAULT | RM | DEFAULT
|  | Value | 7.7 | 9820 | 7.3 | 9820 | 7.3 | 9820

## Compliance Averages
Compliance Averages
This is not an official report. This file contains information used to create the MATS Quarterly Compliance Report
Unit ID or StackPipeID | Averaging Group ID | Parameter | Date | Average Type | Units of Measure | Average Value | Comment
| GP1 | HG | 2025-10-01 | 30D | lb/TBtu | 0.3
| GP1 | HG | 2025-10-02 | 30D | lb/TBtu | 0.31
| GP1 | HG | 2025-10-03 | 30D | lb/TBtu | 0.31
| GP1 | HG | 2025-10-04 | 30D | lb/TBtu | 0.32
| GP1 | HG | 2025-10-05 | 30D | lb/TBtu | 0.33
| GP1 | HG | 2025-10-06 | 30D | lb/TBtu | 0.34
| GP1 | HG | 2025-10-07 | 30D | lb/TBtu | 0.34
| GP1 | HG | 2025-10-08 | 30D | lb/TBtu | 0.35
| GP1 | HG | 2025-10-09 | 30D | lb/TBtu | 0.35
| GP1 | HG | 2025-10-10 | 30D | lb/TBtu | 0.36
| GP1 | HG | 2025-10-11 | 30D | lb/TBtu | 0.37
| GP1 | HG | 2025-10-12 | 30D | lb/TBtu | 0.37
| GP1 | HG | 2025-10-13 | 30D | lb/TBtu | 0.38
| GP1 | HG | 2025-10-14 | 30D | lb/TBtu | 0.39
| GP1 | HG | 2025-10-15 | 30D | lb/TBtu | 0.39
| GP1 | HG | 2025-10-16 | 30D | lb/TBtu | 0.4
| GP1 | HG | 2025-10-17 | 30D | lb/TBtu | 0.41
| GP1 | HG | 2025-10-18 | 30D | lb/TBtu | 0.41
| GP1 | HG | 2025-10-19 | 30D | lb/TBtu | 0.42
| GP1 | HG | 2025-10-24 | 30D | lb/TBtu | 0.43
| GP1 | HG | 2025-10-25 | 30D | lb/TBtu | 0.45
| GP1 | HG | 2025-10-26 | 30D | lb/TBtu | 0.46
| GP1 | HG | 2025-10-27 | 30D | lb/TBtu | 0.48
| GP1 | HG | 2025-10-28 | 30D | lb/TBtu | 0.49
| GP1 | HG | 2025-10-29 | 30D | lb/TBtu | 0.5
| GP1 | HG | 2025-10-30 | 30D | lb/TBtu | 0.51
| GP1 | HG | 2025-10-31 | 30D | lb/TBtu | 0.52
| GP1 | HG | 2025-11-01 | 30D | lb/TBtu | 0.53
| GP1 | HG | 2025-11-02 | 30D | lb/TBtu | 0.54
| GP1 | HG | 2025-11-03 | 30D | lb/TBtu | 0.55
| GP1 | HG | 2025-11-04 | 30D | lb/TBtu | 0.56
| GP1 | HG | 2025-11-05 | 30D | lb/TBtu | 0.57
| GP1 | HG | 2025-11-06 | 30D | lb/TBtu | 0.6
| GP1 | HG | 2025-11-07 | 30D | lb/TBtu | 0.63
| GP1 | HG | 2025-11-08 | 30D | lb/TBtu | 0.65
| GP1 | HG | 2025-11-09 | 30D | lb/TBtu | 0.66
| GP1 | HG | 2025-11-10 | 30D | lb/TBtu | 0.67
| GP1 | HG | 2025-11-11 | 30D | lb/TBtu | 0.69
| GP1 | HG | 2025-11-12 | 30D | lb/TBtu | 0.71
| GP1 | HG | 2025-11-13 | 30D | lb/TBtu | 0.71
| GP1 | HG | 2025-11-14 | 30D | lb/TBtu | 0.71
| GP1 | HG | 2025-11-15 | 30D | lb/TBtu | 0.71
| GP1 | HG | 2025-11-16 | 30D | lb/TBtu | 0.7
| GP1 | HG | 2025-11-17 | 30D | lb/TBtu | 0.69
| GP1 | HG | 2025-11-18 | 30D | lb/TBtu | 0.68
| GP1 | HG | 2025-11-19 | 30D | lb/TBtu | 0.66
| GP1 | HG | 2025-11-20 | 30D | lb/TBtu | 0.66
| GP1 | HG | 2025-11-21 | 30D | lb/TBtu | 0.65
| GP1 | HG | 2025-11-22 | 30D | lb/TBtu | 0.65
| GP1 | HG | 2025-11-23 | 30D | lb/TBtu | 0.64
| GP1 | HG | 2025-11-24 | 30D | lb/TBtu | 0.63
| GP1 | HG | 2025-11-25 | 30D | lb/TBtu | 0.61
| GP1 | HG | 2025-11-26 | 30D | lb/TBtu | 0.6
| GP1 | HG | 2025-11-27 | 30D | lb/TBtu | 0.59
| GP1 | HG | 2025-11-28 | 30D | lb/TBtu | 0.58
| GP1 | HG | 2025-11-29 | 30D | lb/TBtu | 0.57
| GP1 | HG | 2025-11-30 | 30D | lb/TBtu | 0.56
| GP1 | HG | 2025-12-01 | 30D | lb/TBtu | 0.55
| GP1 | HG | 2025-12-02 | 30D | lb/TBtu | 0.54
| GP1 | HG | 2025-12-03 | 30D | lb/TBtu | 0.54
| GP1 | HG | 2025-12-04 | 30D | lb/TBtu | 0.53
| GP1 | HG | 2025-12-05 | 30D | lb/TBtu | 0.52
| GP1 | HG | 2025-12-06 | 30D | lb/TBtu | 0.51
| GP1 | HG | 2025-12-07 | 30D | lb/TBtu | 0.5
| GP1 | HG | 2025-12-08 | 30D | lb/TBtu | 0.48
| GP1 | HG | 2025-12-09 | 30D | lb/TBtu | 0.47
| GP1 | HG | 2025-12-10 | 30D | lb/TBtu | 0.46
| GP1 | HG | 2025-12-11 | 30D | lb/TBtu | 0.44
| GP1 | HG | 2025-12-12 | 30D | lb/TBtu | 0.43
| GP1 | HG | 2025-12-13 | 30D | lb/TBtu | 0.42
| GP1 | HG | 2025-12-14 | 30D | lb/TBtu | 0.42
| GP1 | HG | 2025-12-15 | 30D | lb/TBtu | 0.41
| GP1 | HG | 2025-12-16 | 30D | lb/TBtu | 0.4
| GP1 | HG | 2025-12-17 | 30D | lb/TBtu | 0.4
| GP1 | HG | 2025-12-18 | 30D | lb/TBtu | 0.4
| GP1 | HG | 2025-12-19 | 30D | lb/TBtu | 0.4
| GP1 | HG | 2025-12-20 | 30D | lb/TBtu | 0.39
| GP1 | HG | 2025-12-21 | 30D | lb/TBtu | 0.41
| GP1 | HG | 2025-12-22 | 30D | lb/TBtu | 0.42
| GP1 | HG | 2025-12-23 | 30D | lb/TBtu | 0.42
| GP1 | HG | 2025-12-24 | 30D | lb/TBtu | 0.42
| GP1 | HG | 2025-12-25 | 30D | lb/TBtu | 0.43
| GP1 | HG | 2025-12-26 | 30D | lb/TBtu | 0.44
| GP1 | HG | 2025-12-27 | 30D | lb/TBtu | 0.45
| GP1 | HG | 2025-12-28 | 30D | lb/TBtu | 0.46
| GP1 | HG | 2025-12-29 | 30D | lb/TBtu | 0.46
| GP1 | HG | 2025-12-30 | 30D | lb/TBtu | 0.46
| GP1 | HG | 2025-12-31 | 30D | lb/TBtu | 0.46

## Monitor Downtime
Monitor Downtime/Deviation |  |  | Blank if no downtime to report.
This is not an official report. This file contains information used to create the MATS Quarterly Compliance Report
Unit Stack or Pipe ID | Averaging Group ID | Type | Parameter | Standard | Total (Monitor Downtime) Operating Time | Hours of Deviation | Hours of Downtime | Unmonitored Bypass Hours | Comment
1 |  | Downtime/Deviation | HG | 63.10020(d) | 24 | 0 | 24 |  | performed QA, initiated new traps
2 |  | Downtime/Deviation | HG | 63.10020(d) | 57 | 13 | 57 |  | performed calibration, initiated new traps

## Exceedances
MATS Exceedances |  | Blank if no exceedances to report
This is not an official report. This file contains information used to create the MATS Quarterly Compliance Report
Unit Stack or Pipe ID | Averaging Group ID | Parameter | Limit Exceeded | Begin Date | End Date | Comment

## Late Test
Late Test |  | Blank if no late tests to report
This is not an official report. This file contains information used to create the MATS Quarterly Compliance Report
Unit Stack or Pipe ID | Parameter | Test Deadline | Elapsed Days | Standard | Comment

## Other Deviations
Other Deviations |  | Blank if no other deviations to report
This is not an official report. This file contains information used to create the MATS Quarterly Compliance Report
Unit Stack or Pipe ID | Deviation Type | Standard | Comment

## Malfunction Information
Malfunction Information |  | Used to report control equipment malfunctions that cause exceedances. Blank if no malfunctions to report.
This is not an official report. This file contains information used to create the MATS Quarterly Compliance Report
Unit ID | Event Begin Date/Time | Event End Date/Time | Malfunction Description | Corrective Action